## Slide 1: Environmental factors need to be taken into account within healthcare and other settings
For example
Ceiling systems of a lay-in ceiling tile design should be avoided. Drop ceiling grids, and any plumbing, piping, ductwork or other potentially hazardous elements concealed above a ceiling can be used as a hanging device. The ceiling should be of monolithic construction.
Sprinkler heads should be a flush mounted design.
Door-closer devices should be mounted on the public side of a door versus the private patient side of the door. Ideally, the door-closer (if required) should be within view of a nurse or staff workstation. Door hinges should be of the continuous piano style. Door lever handles should point downward when in the latched position. Note that all hardware should have tamper-resistant fasteners.
Towel bars are not required for American with Disabilities Act (ADA) accessibility compliance; therefore avoiding towel bar installations in private patient rooms is recommended. If provided, towel bars should be designed to not support the weight of the lowest weighted patient served on the unit.
Showerheads should be of the flush mounted design. Push-button shower controls are recommended.
Clothing rods or hooks should be designed to not support the weight of the lowest weighted patient served on the unit.
Horizontal or partially inclined plumbing/utility pipes should be enclosed.
ADA-compliant grab bars are required in 10% of the patient private/semi-private toilet rooms. The remaining 90% are not required to have ADA-compliant grab bars installed unless the patient room is used by a patient with disabilities. Reinforced wall areas for future installation of grab bars should be provided or existing wall capabilities should be verified. Grab bars for fully ambulatory patients should be removed. If grab bars are required for a patient, the bars should be mounted with a continuous rail-to-wall attachment.
Shower curtain rods should be designed to not support the weight of the lowest weighted patient served on the unit.
https://www.dhs.wisconsin.gov/dqa/memos/11-019.pdf Wisconsin
http://www.health.state.mn.us/patientsafety/publications/suicideprevhealthcarefac.pdf Minnesota
Mental Health Environment of Care Checklist VHA National Center for Patient Safety Department of Veterans Affairs Version 03-01-2012 https://www.patientsafety.va.gov/professionals/onthejob/mentalhealth.asp

## Slide 2
Checklist for Assessing Environmental Risks for Suicide
The following is a brief checklist to help hospitals assess and address suicide risks in their ED and medical/surgical units.
❏ Avoid “lay-in” ceilings. These can make it easier for the patient to hide contraband, can provide a convenient place to secure a ligature for self-harm, or may allow the patient access to above-the-ceiling interstitial spaces.
❏ If the outside window of the room is operable, limit the opening so a person could not pass through (4–6 inches is considered the architectural standard of care). Alternatively, consider protecting a window with a security screen that is secured by a device that can be removed from the inside only with a special tool (such as a non-common screw head).
❏ Make window glazing shatter-proof.
❏ Use a tamper-resistant, anti-ligature door knob for the patient’s room.
❏ If a hospital bed is in use, secure the electrical power cord on the bed. Consider replacing the bed cord with a “jumper cord” that can be removed by staff, kept in a secure place, and used only when the bed needs to be adjusted. (Check the bed design to ensure that the bed can be mechanically lowered to a “CPR” position.)
❏ Use tamper-resistant screws throughout the room.
❏ Secure the power cord on the TV. A mounting bracket can be an attachment point for a ligature.
❏ Replace cork bulletin boards with dry-mark boards, thus eliminating inadvertent use of thumbtacks.
❏ Use shatter-proof and tamper-resistant glass in night lights and other lighting fixtures.
❏ Secure light fixtures to restrict patient access to bulbs and sockets.
❏ Remove grab bars in the bathroom or fill in the wall “gap.”
❏ Eliminate coat hooks, towel bars, cubicle curtain tracks, and closet poles.
❏ Ensure that all electrical outlets are GFCI (ground fault circuit interrupter) and tamper resistant.
❏ Replace metal outlet covers with shatter-proof non-conductive covers.
❏ Protect the piping for the toilet and lavatory.
❏ Use tamper-resistant lavatory faucets.
❏ Ensure that HVAC (heating, ventilating, and air conditioning) grills are tamper resistant.
❏ Use tamper-resistant shower controls and shower heads.
❏ Ensure that mirror and picture glazing material are shatter-proof. Source: Adapted from Sine D.M.: Latent risks in the built environment for the behavioral health patient: Concerns for the healthcare risk manager.
In The American Society for Healthcare Risk Management Handbook, 6th ed. Chicago: American Hospital Association, 2010.